## Mariga Health Post
Borehole Solar System BOQ
Schedule Of Rates:
No | Activity | Unit Cost In US$ | Units | Quantity per site | Total cost in US$
Attention is drawn to the General Conditions of Contract, Form of Contract, Specification, Drawings, attached schedules and amendments thereto contained in this document. These documents are to be read in conjunction with the Bill of Quantities
Each item, including zero items, shall be priced with the exception of those items which already have provisional sums attached thereto, if the Contractor omits to price any item, the cost of such items will be deemed to be spread over and included in the prices contracted for other items.
The rates and prices in the Bill of Quantities shall be deemed to cover all the Contractor's obligations under the contract and all matters and things necessary for the proper completion and maintenance of the works.
The Contractor must note that materials for the contract are to be ordered from the working drawings as checked where necessary from site measurements. They must not be ordered from either the Bill of Quantities or the Contract drawings without the written permission of the Engineer.Payment will be based on the actual measured work done onsite
The Contractor shall provide with his Tender submission a detailed breakdown of all priced items of Bill No 1, Preliminaries and General Requirements. This breakdown of the items shall be in a format, which also clearly identifies any "Set - Up" costs and time related charges
The Contractor shall safeguard the Works, materials and plant against damage, loss or injury,including all necessary watching and lighting for the safety and security of the Works and the protection of the public and provide shelter and reasonable accommodation
The contractor shall provide and maintain temporary sheds for the storage of materials, tools, and tackle for use at the Site. Those used for the storage of cement and other perishable materials and the like are to be weatherproofed at all times
Where alternative rates have been called for in the Bill of Quantities, the Engineer reserves the right to use any of the alternative materials or forms of construction.
Where the item in the Bill of Quantities is described as "Provisional" the rate entered against the item holds for any variation in the quantity provisionally billed.
1 | Mobilization & demobilization :
1.1 | Initial Mobilization and Demobilization to the site and back. | 0 | lsum | 1 | US$-
1.1.2 | Sub. Total for Mobilization and Demobilization: |  |  |  | US$-
2 | Borehole testing
2.1.1 | Allow for Site Works -Site Preparation & Clearance after works | US$- | no. | 1 | US$-
2.1.7 | 8 -Hour Capacity Testing | US$- | no. | 1 | US$-
2.1.8 | Water Quality Testing( bacterological and chemical) | US$- | no. | 1 | US$-
2.1.9 | Subtotal |  |  |  | US$-
2 | PV Generator and Water Pumping system
2.1.1 | Supply and install a 2 Hp DC pump and DC controller able and rated to supply the required maximum duty of 1L/s over 140 metres of the design head). | US$- | pump | 1 | US$-
2.1.2 | Supply and install Dry Run Probe (specify if its in built). |  | unit | 1 | US$-
2.1.3 | Supply and install Surge Protector | US$- | unit | 1 | US$-
2.1.4 | Supply and install Lightining Arrestor (specify if its in built). |  | unit | 1 | US$-
2.1.5 | Supply and install 500 Watt solar panels rated to supply 48 volts or 12.84 amps (6 panel per site) | US$- | sites | 1 | US$-
2.1.6 | Allow for supply and installation of a 4mm2 4C FLEX supply cable (provisional length) complete with glands, shrouds, joints, adaptor to pump connection requirements.(150m per site) | US$- | sites | 1 | US$-
2.1.8 | Supply and install Safety rope (cotton braided) (as per proposed borehole depth) | US$- | sites | 1 | US$-
2.1.9 | Supply and install HDPE 40mm Class 12 -down the hole pipe PLUS total | US$- | meter | 100 | US$-
supply line to tap stand.
2.1.10 | Supply and install HDPE 40mm Class 10 -Supply line to storage tanks | US$- | meter | 600 | US$-
(for reticulation)
2.1.11 | Supply and install 40mm G.I base plate complete with connection to start of the 40mm HDPE main supply line.These connections include a 40mm Brass NRV (spring loaded),a 40mm G.I socket union ,G.I elbow connections ). | US$- | unit | 1 | US$-
| Installation of 50mm GI gate valve, Valve boxes, covers and valve markers (provide for fittings to connect to 40mm HDPE pipes) | US$- | No | 2 | US$-
2.1.12 | Subtotal |  |  |  | US$-
3 | Pump Accessories
3.1.1 | Supply and install 1000v/32A PV Disconnect | US$- | unit | 1 | US$-
3.1.2 | Allow for the supply and installation of an approved surface mounted lockable weatherproof borehole distribution board complete with switch gear . Shop floor design drawings to be submitted for approval prior to manufacturer. | US$- | unit | 1 | US$-
manufacture.
3.1.3 | Allow for the supply and installation of an approved weatherproof pump compatible controller with intelligent control box, high voltage and low voltage control, overcurrent/overload protection and MPPT function. | US$- | unit | 1 | US$-
3.1.4 | Supply and install approved 16mm diameter x 1200mm long COPPER earth | US$- | unit | 1 | US$-
electrode.
3.1.5 | Allow for supply and installation of a 4mm2 SBCC complete with crimping lugs for the borehole earthing system. | US$- | meter | 10 | US$-
3.1.6 | Subtotal |  |  |  | US$-
4 | Water Storage System
4.1.1 | Supply and install 5,000 litres water storage tanks.(water tank stand as per | US$- | unit | 2 | US$-
provided drawing)
4.1.2 | Allow for 3m solar stand suitable for 3 Canadian solar panels and the mounting sleeve (refer to drawing for CHS sizes for columns, angles irons for solar frame, and square tubes for support of the panels | US$- | unit | 2 | US$-
4.1.3 | Allow for 4m tank stands suitable for 5 000 litres storage tanks complete with overflow connections (refer to drawing for angle iron sizes for columns, gauge for channel irons for tank stand platforms,and gauge for tank stands | US$- | unit | 2 | US$-
braces).
4.1.4 | Supply and install 40mm GI Pipe fittings and control valves from inlet and to outlet as well as accessories together with overflow pipe on water storage tank | US$- | unit | 2 | US$-
4.1.5 | Allow for construction of Tank stand, Solar Stand, Concrete Pad fountations at Tank stand and solar stand,grouting seal ,Allow for Sanitary seal of borehole).tap stands apron of 0.5m radius and aproved slab thickness | US$- | sites | 1 | US$-
,manhole cover with safety lock as specified )Cement grade 30MPA
4.1.6 | Subtotal |  |  |  | US$-
5 | Water Tap stand/Stand pipe accessories
5.1.1. | Supply and install 20 mm Taps complete with 1m tall support columns c/w accesories.(Each tap to be provided with all fittings required to connect to distribution mainline) | US$- | No | 6 | US$-
5.1.2 | Supply and install HDPE pipe 40 mm class 10 and accessories for reticulation to the water point | US$- | metres | 1000 | US$-
5.1.3 | Allow for One day training on Operations and Maintainance for Water Committee staff | US$- | No | 20 | US$-
and relevant government stakeholders
5.1.1 | Allow for supply and installation of Palisade fencing (4m*5m*2.2m) and installation of 4 by 100W solar flood lights with 5 metres above the ground steel mast | US$- | sites | 1 | US$-
5.1.11 | Subtotal |  |  |  | US$-
5.1.12 | Preliminary and Generals : Allow for milestone stage inspections done in the presence of all relevant government stake hoders. | US$- | unit | 0 | US$-
5.1.13 | Sub Total cost of Piped Water scheme installation , testing and commissioning services and materials: |  |  |  | US$-
5.1.14 | Allow for a provisional sum for any fittings and works not specified above | US$- | sum | 1 | US$-
5.1.15 | SUB Total cost of Borehole Solar System |  |  |  | US$-
5.1.17 | Sub -total cost of Solar Borehole |  |  |  | US$-
5.1.18 | 15% VAT costs on services and Materials for all works in us$ |  |  |  | US$-
5.1.19 | SUB Total cost of Borehole Solar System |  |  |  | US$-
5.1.20 | Additional Costs to be applied for defects maintennce and back up support | Unit Cost In US$ | Units | Quantity per PWS | Cost in US$ per meter
6 | NOTE: This section covers additional works as and when required. Contractors are requested to quote individual rates per meter for additional pipe lengths that may become neccessary. This rate will be calculated and included when the installation works are completed and when the final Invoice is being prepared. |  |  |  | 0
6.1.1 | Optional and or additional estimated costs of services and Material cost for incidental works in US$: |  | rate/metre
| SUB Total cost of Borehole Solar System |  |  |  | 0
6.1.2 | NB: Section 6 (and its sub-sections) will only be applicable as and when the contract requires the supply and installation of addtional pipe lengths upon prior approval by Campfire. Section 6 will only be applicable as and when the context requires and shall be upon prior approval by CLIENT.

## Masoka Camp
Borehole Solar System BOQ
Schedule Of Rates:
No | Activity | Unit Cost In US$ | Units | Quantity per site | Total cost in US$
Attention is drawn to the General Conditions of Contract, Form of Contract, Specification, Drawings, attached schedules and amendments thereto contained in this document. These documents are to be read in conjunction with the Bill of Quantities
Each item, including zero items, shall be priced with the exception of those items which already have provisional sums attached thereto, if the Contractor omits to price any item, the cost of such items will be deemed to be spread over and included in the prices contracted for other items.
The rates and prices in the Bill of Quantities shall be deemed to cover all the Contractor's obligations under the contract and all matters and things necessary for the proper completion and maintenance of the works.
The Contractor must note that materials for the contract are to be ordered from the working drawings as checked where necessary from site measurements. They must not be ordered from either the Bill of Quantities or the Contract drawings without the written permission of the Engineer.Payment will be based on the actual measured work done onsite
The Contractor shall provide with his Tender submission a detailed breakdown of all priced items of Bill No 1, Preliminaries and General Requirements. This breakdown of the items shall be in a format, which also clearly identifies any "Set - Up" costs and time related charges
The Contractor shall safeguard the Works, materials and plant against damage, loss or injury,including all necessary watching and lighting for the safety and security of the Works and the protection of the public and provide shelter and reasonable accommodation
The contractor shall provide and maintain temporary sheds for the storage of materials, tools, and tackle for use at the Site. Those used for the storage of cement and other perishable materials and the like are to be weatherproofed at all times
Where alternative rates have been called for in the Bill of Quantities, the Engineer reserves the right to use any of the alternative materials or forms of construction.
Where the item in the Bill of Quantities is described as "Provisional" the rate entered against the item holds for any variation in the quantity provisionally billed.
1 | Mobilization & demobilization :
1.1 | Initial Mobilization and Demobilization to the site and back. | 0 | lsum | 1 | US$-
1.1.2 | Sub. Total for Mobilization and Demobilization: |  |  |  | US$-
2 | Borehole testing
2.1.1 | Allow for Site Works -Site Preparation & Clearance after works | US$- | no. | 1 | US$-
2.1.7 | 8 -Hour Capacity Testing | US$- | no. | 1 | US$-
2.1.8 | Water Quality Testing( bacterological and chemical) | US$- | no. | 1 | US$-
2.1.9 | Subtotal |  |  |  | US$-
2 | PV Generator and Water Pumping system
2.1.1 | Supply and install a 2 Hp DC pump and DC controller able and rated to supply the required maximum duty of 1L/s over 140 metres of the design head). | US$- | pump | 1 | US$-
2.1.2 | Supply and install Dry Run Probe (specify if its in built). |  | unit | 1 | US$-
2.1.3 | Supply and install Surge Protector | US$- | unit | 1 | US$-
2.1.4 | Supply and install Lightining Arrestor (specify if its in built). |  | unit | 1 | US$-
2.1.5 | Supply and install 500 Watt solar panels rated to supply 48 volts or 12.84 amps (6 panel per site) | US$- | sites | 1 | US$-
2.1.6 | Allow for supply and installation of a 4mm2 4C FLEX supply cable (provisional length) complete with glands, shrouds, joints, adaptor to pump connection requirements.(150m per site) | US$- | sites | 1 | US$-
2.1.8 | Supply and install Safety rope (cotton braided) (as per proposed borehole depth) | US$- | sites | 1 | US$-
2.1.9 | Supply and install HDPE 40mm Class 12 -down the hole pipe PLUS total | US$- | meter | 100 | US$-
supply line to tap stand.
2.1.10 | Supply and install HDPE 40mm Class 10 -Supply line to storage tanks | US$- | meter | 500 | US$-
(for reticulation)
2.1.11 | Supply and install 40mm G.I base plate complete with connection to start of the 40mm HDPE main supply line.These connections include a 40mm Brass NRV (spring loaded),a 40mm G.I socket union ,G.I elbow connections ). | US$- | unit | 1 | US$-
| Installation of 50mm GI gate valve, Valve boxes, covers and valve markers (provide for fittings to connect to 40mm HDPE pipes) | US$- | No | 2 | US$-
2.1.12 | Subtotal |  |  |  | US$-
3 | Pump Accessories
3.1.1 | Supply and install 1000v/32A PV Disconnect | US$- | unit | 1 | US$-
3.1.2 | Allow for the supply and installation of an approved surface mounted lockable weatherproof borehole distribution board complete with switch gear . Shop floor design drawings to be submitted for approval prior to manufacturer. | US$- | unit | 1 | US$-
manufacture.
3.1.3 | Allow for the supply and installation of an approved weatherproof pump compatible controller with intelligent control box, high voltage and low voltage control, overcurrent/overload protection and MPPT function. | US$- | unit | 1 | US$-
3.1.4 | Supply and install approved 16mm diameter x 1200mm long COPPER earth | US$- | unit | 1 | US$-
electrode.
3.1.5 | Allow for supply and installation of a 4mm2 SBCC complete with crimping lugs for the borehole earthing system. | US$- | meter | 10 | US$-
3.1.6 | Subtotal |  |  |  | US$-
4 | Water Storage System
4.1.1 | Supply and install 5,000 litres water storage tanks.(water tank stand as per | US$- | unit | 2 | US$-
provided drawing)
4.1.2 | Allow for 3m solar stand suitable for 3 Canadian solar panels and the mounting sleeve (refer to drawing for CHS sizes for columns, angles irons for solar frame, and square tubes for support of the panels | US$- | unit | 2 | US$-
4.1.3 | Allow for 4m tank stands suitable for 5 000 litres storage tanks complete with overflow connections (refer to drawing for angle iron sizes for columns, gauge for channel irons for tank stand platforms,and gauge for tank stands | US$- | unit | 2 | US$-
braces).
4.1.4 | Supply and install 40mm GI Pipe fittings and control valves from inlet and to outlet as well as accessories together with overflow pipe on water storage tank | US$- | unit | 2 | US$-
4.1.5 | Allow for construction of Tank stand, Solar Stand, Concrete Pad fountations at Tank stand and solar stand,grouting seal ,Allow for Sanitary seal of borehole).tap stands apron of 0.5m radius and aproved slab thickness | US$- | sites | 1 | US$-
,manhole cover with safety lock as specified )Cement grade 30MPA
4.1.6 | Subtotal |  |  |  | US$-
5 | Water Tap stand/Stand pipe accessories
5.1.1. | Supply and install 20 mm Taps complete with 1m tall support columns c/w accesories.(Each tap to be provided with all fittings required to connect to distribution mainline) | US$- | No | 6 | US$-
5.1.2 | Supply and install HDPE pipe 40 mm class 10 and accessories for reticulation to the water point | US$- | metres | 600 | US$-
5.1.3 | Allow for One day training on Operations and Maintainance for Water Committee staff | US$- | No | 20 | US$-
and relevant government stakeholders
5.1.1 | Allow for supply and installation of Palisade fencing (4m*5m*2.2m) and installation of 4 by 100W solar flood lights with 5 metres above the ground steel mast | US$- | sites | 1 | US$-
5.1.11 | Subtotal |  |  |  | US$-
5.1.12 | Preliminary and Generals : Allow for milestone stage inspections done in the presence of all relevant government stake hoders. | US$- | unit | 0 | US$-
5.1.13 | Sub Total cost of Piped Water scheme installation , testing and commissioning services and materials: |  |  |  | US$-
5.1.14 | Allow for a provisional sum for any fittings and works not specified above | US$- | sum | 1 | US$-
5.1.15 | SUB Total cost of Borehole Solar System |  |  |  | US$-
5.1.17 | Sub -total cost of Solar Borehole |  |  |  | US$-
5.1.18 | 15% VAT costs on services and Materials for all works in us$ |  |  |  | US$-
5.1.19 | SUB Total cost of Borehole Solar System |  |  |  | US$-
5.1.20 | Additional Costs to be applied for defects maintennce and back up support | Unit Cost In US$ | Units | Quantity per PWS | Cost in US$ per meter
6 | NOTE: This section covers additional works as and when required. Contractors are requested to quote individual rates per meter for additional pipe lengths that may become neccessary. This rate will be calculated and included when the installation works are completed and when the final Invoice is being prepared. |  |  |  | 0
6.1.1 | Optional and or additional estimated costs of services and Material cost for incidental works in US$: |  | rate/metre
| SUB Total cost of Borehole Solar System |  |  |  | 0
6.1.2 | NB: Section 6 (and its sub-sections) will only be applicable as and when the contract requires the supply and installation of addtional pipe lengths upon prior approval by Campfire. Section 6 will only be applicable as and when the context requires and shall be upon prior approval by CLIENT.